## Sheet1
Filter Selection Based on OMEGA Catalog
| Flow Rate | 500 | Nm3/hr | According to PID and DSH
| Pressure | 1 | Barg | According to PID and DSH
| Particle Class | 1 | -- | According to ISO 8573-1 or Concentration
| Oil Class | 1 | -- | According to ISO 8573-1 or Concentration
Correction Factor
| Operating Pressure (Bar) |  |  | 2 | 3 | 4 | 5 | 6 | 7 |  | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| Operating Pressure (PSI) |  |  | 29 | 43 | 58 | 72 | 87 | 100 |  | 115 | 130 | 145 | 160 | 174 | 189 | 203 | 218 | 232
| Correction Factor |  |  | 0.38 | 0.5 | 0.63 | 0.75 | 0.88 | 1 |  | 1.13 | 1.25 | 1.38 | 1.5 | 1.63 | 1.75 | 1.88 | 2 | 2.13
Interpolation
| Pressure | Corr. Factor
| 8 | 1.13
| 8 | 1.13
| 8 | 1.13
| Filter Housing Size |  | Pipe Size (inch) | Max Oper. Pressure (Bar/PSI) - Nm3/hr |  |  | Flow Rate @ 7 barg 20° |  |  | Element
| AF 0056 |  | 3/8" | 16 / 232 |  |  | 60 |  |  | 1 x 06050
| AF 0076 |  | 1/2" | 16 / 232 |  |  | 78 |  |  | 1 x 07050
| AF 0106 |  | 3/4" | 16 / 232 |  |  | 120 |  |  | 1 x 14050
| AF 0186 |  | 1" | 16 / 232 |  |  | 198 |  |  | 1 x 12075
| AF 0306 |  | 1" | 16 / 232 |  |  | 335 |  |  | 1 x 22075
| AF 0476 |  | 11/2" | 16 / 232 |  |  | 510 |  |  | 1 x 32075
| AF 0706 |  | 11/2" | 16 / 232 |  |  | 780 |  |  | 1 x 50075
| AF 0946 |  | 2" | 16 / 232 |  |  | 1000 |  |  | 1 x 51090
| AF 1506 |  | 2" | 16 / 232 |  |  | 1500 |  |  | 1 x 76090
| AF 1756 |  | 21/2" | 16 / 232 |  |  | 1680 |  |  | 1 x 76090
| AF 2006 |  | 3" | 16 / 232 |  |  | 2160 |  |  | 1 x 51140
| AF 2406 |  | 3" | 16 / 232 |  |  | 2760 |  |  | 1 x 75140
| HF 4000 |  | 16", Sch.20 | 16 / 232 |  |  | 4320 |  |  | 2 x 51140
| HF 5000 |  | 16", Sch.20 | 16 / 232 |  |  | 5520 |  |  | 2 x 75140
| HF 6000 |  | 16", Sch.20 | 16 / 232 |  |  | 6480 |  |  | 3 x 51140
| HF 8000 |  | 16", Sch.20 | 16 / 232 |  |  | 8280 |  |  | 3 x 75140
| HF 10000 |  | 18", Sch.20 | 16 / 232 |  |  | 11040 |  |  | 4 x 75140
| HF 12000 |  | 24", Sch.20 | 16 / 232 |  |  | 12960 |  |  | 6 x 51140
| HF 14000 |  | 24", Sch.20 | 16 / 232 |  |  | 15120 |  |  | 7 x 51140
| HF 16000 |  | 24", Sch.20 | 16 / 232 |  |  | 16560 |  |  | 6 x 75140
| HF 18000 |  | 24", Sch.20 | 16 / 232 |  |  | 19440 |  |  | 9 x 51140
| HF 22000 |  | 24", Sch.20 | 16 / 232 |  |  | 22080 |  |  | 8 x 75140
| HF 24000 |  | 24", Sch.20 | 16 / 232 |  |  | 24840 |  |  | 9 x 75140
| Calculation: |  | 442.4779 |  |  | Calculation: |  | 376.1062
| AF 2006 | 0.20485 | 1 | 1717.5221
| AF 2406 | 0.16032 | 1 | 2317.5221
| Filter Type for pre-filter |  | AF 0476 | 1 x 32075 |  | Filter Type for after-filter |  | AF 0476 | 1 x 32075
Table 2 - Solid particle classes Based On ISO-8573
| class |  | Partical Size (ɥm) |  |  |  | Partical Size (ɥm) |  | Concentration (mg/m3)
|  |  | ≤ 0.1 | 0.1 < d ≤ 0.5 | 0.5 < d ≤ 1 | 1 < d ≤ 5
| 0 |  | As specified by the equipment user or supplier and more stringent than class 1 |  |  |  | Not applicable |  | Not applicable
| 1 |  | Not Specified | 100 | 1 | 0
| 2 |  | Not Specified | 100000 | 1000 | 10
| 3 |  | Not Specified | Not Specified | 10000 | 500
| 4 |  | Not Specified | Not Specified | Not Specified | 1000
| 5 |  | Not Specified | Not Specified | Not Specified | 20000
| 6 |  | Not Applicable |  |  |  | ≤ 5 |  | ≤ 5
| 7 |  | Not Applicable |  |  |  | ≤ 40 |  | ≤ 10
Table 5 - Oil Classes Based On ISO-8573
| class |  | Concentration total oil (aerosol, liquid, and vapour) mg/m3
| 0 |  | As specified by the equipment user or supplier and more stringent than class 1
| 1 |  | ≤ 0.01
| 2 |  | ≤ 0.1
| 3 |  | ≤ 1
| 4 |  | ≤ 5
FILTER ELEMENTS (OMEGA)
|  | B sintered 15 μm | P prefilter 3 μm | R prefilter 1 μm | M microfilter 0.1 μm | S microfilter 0.01 μm | A activated carbon | A2 adsorption (act. carbon) | H2 catalyst (hopcalite) | MS2 molecular sieve
| Quality Class Solids | 7 | 6 | 3 | 2 | 1 | 13) | 13) | 13) | 1
| Quality Class Oils | -- | -- | -- | 2 | 1 | 1 | 0/1 | -- | --
| Pressure Drop new element [mbar / psi] | 20 / 0.29 | 10 / 0.145 | 20 / 0.290 | 50 / 0.725 | 80 / 1.160 | 60 / 0.870 | See Spec. | See Spec. | < 50 / 0.725
| Change filter cartridge at pressure drop [mbar / psi] | 1) | 350 / 5,07 | 350 / 5,07 | 350 / 5,07 | 350 / 5,07 | 6 months 2) | 6 months 2) | 6 months 2) | --
1) B filter element can be cleaned with ultrasonic bath or with back flushing. Intervals of cleaning depends of application. If necessary replace filter element with new one.
2) Filter elements ’’A, A2, H2’’, must be changed periodically to suit application, but at least every 6 months. Activated carbon filters must not operate in oil saturated conditions.
3) Valid if ''S'' filter cartridge is installed upstream.
| Pre-Filter Element |  | AF MS |  |  |  | Pre-Filter type |  | AF 0476 | 1 x 32075
| After-Filter Element |  | AF S |  |  |  | After-Filter type |  | AF 0476 | 1 x 32075

## Evaluation Warning
Created with a trial version of Syncfusion Essential XlsIO